## PP-1
Demo Project
VOLTAGE: | MISSING | [11 empty] | LOCATION: | MISSING
PHASE: | MISSING | [11 empty] | FED FROM: | MISSING
‘gHoy JII08HS | MISSING |  |  |  |  | 09 | [6 empty] | UL LISTED EQUIPMENT SHORT CIRCUIT RATING: | MISSING
&@%%& d349HgD | MISSING |  |  |  |  | 31 | [6 empty] | MAXIMUM AVAILABLE SHORT CIRCUIT CURRENT: | MISSING
0 ‘MHzo o | MISSING |  |  |  |  | 498 | [6 empty] | PHASE CONDUCTOR: | MISSING
LOHE86d.9C | MISSING |  |  |  |  | 204 | [6 empty] | NEUTRAL CONDUCTOR: | MISSING
N2J10 — Youeiq | MISSING |  |  |  |  | 1 | [6 empty] | ELECTRICAL GROUND CONDUCTOR: | MISSING
jaq Juswdinbe | MISSING |  |  |  |  | 810
InIT-¥-Mod |  | PHASE AMPS |  | BREAKER |  | 9 |  |  | BREAKER |  |  | PHASE AMPS
WWRH-131NY | PH. A | PH. B | PH. C | POLE | AMP | 13 | PHASE | CKT. | AMP | POLE | PH. A | PH. B | PH. C | LOAD DESCRIPTION & LOCATION
GATE #1 HOIST MOTOR | 11 |  |  | 3 | 20 | 1 | A | 2 | 20 | 3 | 11 |  |  | GATE HOIST #13 MOTOR
- |  | 11 |  | - | - |  | B |  | 20 | - |  | 11 |  | -
- |  |  | 11 | - | - |  | C |  | 20 | - |  |  | 11 | -
GATE #2 HOIST MOTOR | 11 |  |  | 3 | 20 | 3 | A | 4 | 20 | 1 | 0 |  |  | SPARE
- |  | 11 |  | - | - |  | B |  | 20 | 1 |  | 0 |  | SPARE
- |  |  | 11 | - | - |  | C |  | 20 | 1 |  |  | 2 | CONTACTOR CONTROL CIRCUIT
GATE #3 HOIST MOTOR | 11 |  |  | 3 | 20 | 5 | A | 6 | 20 | 3 | 11 |  |  | GATE #9 HOIST MOTOR
- |  | 11 |  | - | - |  | B |  | - | - |  | 11 |  | -
- |  |  | 11 | - | - |  | C |  | - | - |  |  | 11 | -
GATE #4 HOIST MOTOR | 11 |  |  | 3 | 20 | 7 | A | 8 | 20 | 3 | 11 |  |  | GATE #10 HOIST MOTOR
- |  | 11 |  | - | - |  | B |  | - | - |  | 11 |  | -
- |  |  | 11 | - | - |  | C |  | - | - |  |  | 11 | -
GATE #5 HOIST MOTOR | 11 |  |  | 3 | 20 | 9 | A | 10 | 20 | 3 | 11 |  |  | GATE #11 HOIST MOTOR
- |  | 11 |  | - | - |  | B |  | - | - |  | 11 |  | -
- |  |  | 11 | - | - |  | C |  | - | - |  |  | 11 | -
GATE #6 HOIST MOTOR | 11 |  |  | 3 | 20 | 11 | A | 12 | 20 | 3 | 11 |  |  | GATE #12 HOIST MOTOR
- |  | 11 |  | - | - |  | B |  | - | - |  | 11 |  | -
- |  |  | 11 | - | - |  | C |  | - | - |  |  | 11 | -
GATE #7 HOIST MOTOR | 11 |  |  | 3 | 20 | 13 | A | 14 | 20 | 1 | 3 |  |  | LIGHTING HOIST 1, 3, 5, 7, 9, 11, 13
- |  | 11 |  | - | - |  | B |  | 20 | 1 |  | 3 |  | LIGHTING HOIST 2, 4, 6, 8, 12, 12, 14
- |  |  | 11 | - | - |  | C |  | 20 | 1 |  |  | 0 | SPARE
GATE #8 HOIST MOTOR | 11 |  |  | 3 | 20 | 15 | A | 16 | 20 | 1 | 0 |  |  | SPARE
- |  | 11 |  | - | - |  | B |  | 20 | 1 |  | 0 |  | SPARE
- |  |  | 11 | - | - |  | C |  | 20 | 1 |  |  | 0 | SPARE
SPACE |  |  |  | 3 | - | 17 | A | 18 | 30 | 3 | 2 |  |  | SPD
- |  |  |  | - | - |  | B |  | - | - |  | 2 |  | -
- |  |  |  | - | - |  | C |  | - | - |  |  | 2 | -
SPACE |  |  |  | 3 | - | 19 | A | 20 | - | 3 |  |  |  | SPACE
- |  |  |  | - | - |  | B |  | - | - |  |  |  | -
- |  |  |  | - | - |  | C |  | - | - |  |  |  | -
TOTAL AMPS | 88 | 88 | 88 | [7 empty] | 60 | 60 | 59 | TOTAL AMPS
[6 empty] | PH. A | PH. B | PH. C | NOTES:
[5 empty] | TOTAL PHASE AMPS | 148 | 148 | 147
[5 empty] | TOTAL PHASE KVA | 40.996 | 40.996 | 40.719
[5 empty] | TOTAL 3-PHASE KVA |  | 122.711