## PP-1
PP-1
VOLTAGE: | 480/277V | [11 empty] | LOCATION: | ELEC. EQUIP. PAD
PHASE: | 3 | [11 empty] | FED FROM: | MDP AND ATS #1
WIRE: | 4 | [11 empty] | UL LISTED EQUIPMENT SHORT CIRCUIT RATING: | 65K
MAIN BUS AMPS: | 225A | [11 empty] | MAXIMUM AVAILABLE SHORT CIRCUIT CURRENT: | N/A
MAIN CIRCUIT BREAKER: | MLO | [11 empty] | PHASE CONDUCTOR: | #4/0
MOUNTING: | SURFACE | [11 empty] | NEUTRAL CONDUCTOR: | #4/0
FEED: | BOTTOM | [11 empty] | ELECTRICAL GROUND CONDUCTOR: | #4
FEED-THRU LUGS: | NO
|  | PHASE AMPS |  | BREAKER |  |  |  |  | BREAKER |  |  | PHASE AMPS
LOAD DESCRIPTION & LOCATION | PH. A | PH. B | PH. C | POLE | AMP | CKT. | PHASE | CKT. | AMP | POLE | PH. A | PH. B | PH. C | LOAD DESCRIPTION & LOCATION
GATE #1 HOIST MOTOR | 11 |  |  | 3 | 20 | 1 | A | 2 | 20 | 3 | 11 |  |  | GATE HOIST #13 MOTOR
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: 20; BREAKER POLE: -; PHASE AMPS PH. B: 11 | -
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: 20; BREAKER POLE: -; PHASE AMPS PH. C: 11 | -
GATE #2 HOIST MOTOR | 11 |  |  | 3 | 20 | 3 | A | 4 | 20 | 1 | 0 |  |  | SPARE
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: 20; BREAKER POLE: 1; PHASE AMPS PH. B: 0 | SPARE
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: 20; BREAKER POLE: 1; PHASE AMPS PH. C: 2 | CONTACTOR CONTROL CIRCUIT
GATE #3 HOIST MOTOR | 11 |  |  | 3 | 20 | 5 | A | 6 | 20 | 3 | 11 |  |  | GATE #9 HOIST MOTOR
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. B: 11 | -
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. C: 11 | -
GATE #4 HOIST MOTOR | 11 |  |  | 3 | 20 | 7 | A | 8 | 20 | 3 | 11 |  |  | GATE #10 HOIST MOTOR
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. B: 11 | -
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. C: 11 | -
GATE #5 HOIST MOTOR | 11 |  |  | 3 | 20 | 9 | A | 10 | 20 | 3 | 11 |  |  | GATE #11 HOIST MOTOR
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. B: 11 | -
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. C: 11 | -
GATE #6 HOIST MOTOR | 11 |  |  | 3 | 20 | 11 | A | 12 | 20 | 3 | 11 |  |  | GATE #12 HOIST MOTOR
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. B: 11 | -
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. C: 11 | -
GATE #7 HOIST MOTOR | 11 |  |  | 3 | 20 | 13 | A | 14 | 20 | 1 | 3 |  |  | LIGHTING HOIST 1, 3, 5, 7, 9, 11, 13
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: 20; BREAKER POLE: 1; PHASE AMPS PH. B: 3 | LIGHTING HOIST 2, 4, 6, 8, 12, 12, 14
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: 20; BREAKER POLE: 1; PHASE AMPS PH. C: 0 | SPARE
GATE #8 HOIST MOTOR | 11 |  |  | 3 | 20 | 15 | A | 16 | 20 | 1 | 0 |  |  | SPARE
- | PHASE AMPS PH. B: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: 20; BREAKER POLE: 1; PHASE AMPS PH. B: 0 | SPARE
- | PHASE AMPS PH. C: 11; BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: 20; BREAKER POLE: 1; PHASE AMPS PH. C: 0 | SPARE
SPACE |  |  |  | 3 | - | 17 | A | 18 | 30 | 3 | 2 |  |  | SPD
- | BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: B; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. B: 2 | -
- | BREAKER POLE: -; BREAKER AMP: -; BREAKER PHASE: C; BREAKER AMP: -; BREAKER POLE: -; PHASE AMPS PH. C: 2 | -
SPACE | BREAKER POLE: 3; BREAKER AMP: -; BREAKER CKT.: 19; BREAKER PHASE: A; BREAKER CKT.: 20; BREAKER AMP: -; BREAKER POLE: 3 | SPACE
- | [13 empty] | - | bar: BREAKER POLE to BREAKER AMP; BREAKER PHASE; BREAKER AMP to BREAKER POLE
- | [13 empty] | - | bar: BREAKER POLE to BREAKER AMP; BREAKER PHASE; BREAKER AMP to BREAKER POLE
TOTAL AMPS | PH. A: 88; PHASE AMPS PH. B: 88; PHASE AMPS PH. C: 88; BREAKER PH. A: 60; PHASE AMPS PH. B: 60; PHASE AMPS PH. C: 59 | TOTAL AMPS
[6 empty] | PH. A | PH. B | PH. C | NOTES:
[5 empty] | TOTAL PHASE AMPS | 148 | 148 | 147
[5 empty] | TOTAL PHASE KVA | 40.996 | 40.996 | 40.719
[5 empty] | TOTAL 3-PHASE KVA |  | 122.711